## IEC 62040 (hidden)
| IEC 62040-3 Subclause | Declared Characteristics | Manufacturer’s Declared Values
| (except if otherwise noted) | Model (manufacturer’s reference)
General Characteristics |  | Power, rated - Apparent |  | VA
|  | Active |  | W
| 5.1.1 | UPS Configuration
| 5.3.4 | Performance Classification
Mechanical
|  | Dimensions (height*width*depth) |  | mm
|  | Mass |  | kg
|  | Mass with batteries (if integrated) |  | kg
| 6.5.5 | Acoustic noise at 1 m: -Normal Mode |  | dBA
|  | Stored energy mode |  | dBA
Safety
| IEC 62040-1 | Access (operator access or restricted access)
|  | Degree of protection against hazard and water ingress |  | IP
Electromagnetic compatibility
| IEC 62040-2 | Emission |  | UPS Cat
|  | Immunity |  | UPS Cat
Environmental
| 4.2.1.1 | Ambient temperature range |  | deg C
|  | Relative humidity range |  | %
| 4.2.1.2 | Altitude |  | m
| 4.3 | Additional or unusual conditions
| 5.6 | Communication Circuits
(List communication /signalling circuits)
Output Characteristics (Electrical) | 5.3.2 | AC power distribution system
-compatibility (TN,TT,IT)
-phases available (1,2 or 3)
-neutral available (yes/no)
Voltage (steady state, r.m.s)
-normal mode variation
-stored energy mode variation
Total harmonic distortion, 100 % load -normal mode
|  | - linear |  | %
|  | Non-linear |  | %
|  | - stored energy mode, linear |  | %
|  | Non-linear |  | %
|  | Voltage unbalance and phase displacement, 100 % load unbalanced |  | % , °
Voltage transient and recovery time, 100 % step load
|  | -linear |  | %,s
|  | -non-linear |  | %,s
| 6.4.2.11.1/2 | - transfer normal mode / storage energy mode |  | %, s
|  | Frequency (steady-state) - rated |  | Hz
|  | - normal mode variation |  | %
|  | - stored energy mode variation |  | %
|  | - free-running variation |  | %
|  | Synchronization (max ± % range of rated frequency) |  | %
|  | Max synch phase error (referred to a 360° cycle) |  | °
|  | Max slew-rate |  | Hz/s
|  | Current (r.m.s.) - rated |  | A
| 5.3.2.l | - Overload capability (% of rated current / time duration) |  | % / s
|  | - Limitation (% of rated current / time duration) |  | % / s
| 6.4.2.10.3 /4 | - Fault clearing capability (normal / stored energy mode) |  | A gL fuse
Load power factor - rated
- displacement (permissible lead-lag range)
| 5.3.2 r) /6.4.1.6 | AC/ a.c efficiency in normal mode - 100 % load |  | %
| 5.3.2 r) /6.4.1.6 | -75% Load |  | %
| 5.3.2 r) /6.4.1.6 | -50% Load |  | %
| 5.3.2 r) /6.4.1.6 | -25% Load |  | %
Bypass – automatic (static or electro-mechanical)
|  | Transfer time break |  | ms
|  | rated current |  | A
| 5.3.2.1 | Overload current (% of rated current / time duration) |  | % / s
- maintenance (internal or external)
- isolation transformer (yes / no )
Bypass protection fuse or circuit breaker rating
| 5.5 | Stand-alone switch (list any and its product standard)
| 5.3.3 | Additional or unusual conditions
Declared Characteristics Input (Electrical) | 5.2.1.a | Voltage (steady-state, r.m.s) - rated |  | V
| 5.2.1.b | - tolerance |  | %
| 5.2.1.c | Frequency (steady-state) - rated |  | Hz
| 5.2.1.d | - tolerance |  | %
| 5.2.2.c | Current r.m.s. – rated (with the energy storage device charged) |  | A
| 5.2.2.f | maximum (with low input volt and energy storage device charging) |  | A
| 5.2.2.h | -total harmonic distortion (THD p.u.) |  | %
| 5.2.2.g | overload (% of rated current against time) |  | %,s
| 5.2.2.e | in-rush (% of rated current against time) |  | %,s
| 5.2.2.d | power factor |  |  | s
| 5.2.2.k | AC power distribution systems - (TN, TT, IT) compatibility |  |  | s
| 5.2.2.i | - short-circuit power required |  | Ssc
| 5.2.2.a | -phases required (1,2 or 3)
| 5.2.2.b | neutral required (yes/no)
| 5.2.3 | Additional or unusual conditions
Declared Characteristics Battery/stored energy device | 5.4.2.2d | Technology
| 5.4.2.2a | Design life or float service life
| 5.4.2.2b | Quantity of cells and strings
| 5.4.2.2c | Nominal voltage (total)
| 5.4.2.2e | Nominal Ah capacity (C10) |  | Ah
| 5.4.2.2f | Stored energy time (back-up time at 100 % rated load)
| 5.4.2.2g | Restored energy time (recharge time to 90 % capacity)
| 5.4.2.2h | Ambient reference temperature |  | °C
| 5.4.2.2i | Earth condition / Isolation
| 5.4.2.2j | r.m.s. ripple current |  | %
| 5.4.2.2k | Nominal discharge current |  | A
| 5.4.2.2l | Fault current rating |  | A d.c.
| 5.4.2.2m | Cable volt drop recommendation (£ % at nominal discharge current) |  | %
| 5.4.2.2n | Protection requirements by others
| 5.4.2.2o | Charging regime
| 5.4.2.2p | Charge voltage (float boost) and tolerance band |  | V d.c
| 5.4.2.2q | End of discharge voltage |  | V d.c
| 5.4.2.2r | Charge current limit (or range) |  | A d.c.
| 5.4.2..3 | Additional or unusual conditions

## Notes
ENERGY STAR® Power and Performance Data Sheet (PPDS) for Uninterruptible Power Supplies (UPSs) Version 1.0
Enclosed is the PPDS form that shall be completed for each ENERGY STAR qualified UPS upon the finalization of the specification. Please note that this PPDS is in draft form and still under development. EPA seeks comments on the contents (edits, additions, exclusions, etc.) of the PPDS--the formatting and layout of the document will be addressed at a later date. EPA wishes to collaborate with stakeholders in determining its applicability and asks for stakeholders to submit comments and feedback pertaining to the PPDS by Thursday, August 11, 2011. If you have any questions concerning this PPDS, please contact RJ Meyers, EPA, at Meyers.Robert@epamail.epa.gov or 202-343-9923, or Matt Malinowski, ICF International, at MMalinowski@icfi.com or 202-862-2693. For more information on ENERGY STAR UPS specification development, please visit www.energystar.gov/NewSpecs and follow the link for “Uninterruptible Power Supplies."
97+

## ENERGY STAR- DATA ASSEMBLY (hidden)
# | FIELD | VALUE | UNITS | NOTES
PRODUCT DESCRIPTION
1 | Manufacturer |  | –
2 | Model Number |  | –
UPS CONFIGURATION
3 | Topology |  | – |  | Passive-standby | Line-interactive | Double-conversion | Other (Please specify)
4 | Description of normal mode under test |  | – |  | Lowest efficiency/highest protection | Highest efficiency/lowest protection | Other (Please specify)
5 | Maximum time for UPS to switch to highest-protection mode |  | ms
6 | Redundancy |  | – |  | N+0 | N+1 | 2N
7 | Is UPS Modular? |  | – |  | YES | NO
8 | If so, is this minimum or maximum configuration? |  | – |  | Minimum | Maximum
RATED POWER (FOR CONFIGURATION TESTED) | RATED POWER
9 | Apparent |  | VA
10 | Active |  | W
ELECTRICAL INPUT CHARACTERISTICS (FOR CONFIGURATION TESTED)
11 | Rated input voltage range |  | V
12 | Rated input frequency range |  | Hz
13 | Nominal input voltage used for test |  | V |  | 600∆ VAC | 600Y/346 VAC | 480∆ VAC | 480Y/277 VAC | 415∆ VAC | 415Y/240 VAC | 400∆ VAC | 400Y/230 VAC | 208∆ | 208Y/120 VAC | 200 VAC | 100 VAC
14 | Input AC power system compatibility (grounding system) |  | – |  | TN | TT | IT
15 | Number of input phases |  | – |  | 1 | 2 | 3
16 | Is neutral available at input? |  | – |  | YES | NO
ELECTRICAL OUTPUT CHARACTERISTICS (NOT ALL FIELDS APPLICABLE TO DC-OUTPUT SYSTEMS)
17 | Rated output voltage range |  | V
18 | Rated output frequency range |  | Hz
19 | Nominal output voltage used for test |  | V |  | 600∆ VAC | 600Y/346 VAC | 480∆ VAC | 480Y/277 VAC | 415∆ VAC | 415Y/240 VAC | 400∆ VAC | 400Y/230 VAC | 208∆ | 208Y/120 VAC | 200 VAC | 100 VAC | 380 VDC | 60 VDC | 48 VDC | 24 VDC
20 | Output AC power system compatibility (grounding system) |  | – |  | TN | TT | IT
21 | Number of output phases |  | – |  | 1 | 2 | 3
22 | Is neutral available at output? |  | – |  | YES | NO
OUTPUT PERFORMANCE CLASSIFICATION (In accordance with coding AAA BB CCC - Please provide as much information as possible) | PERFORMANCE CLASSIFICATION (In accordance with coding AAA BB CCC)
23 | AAA = Input dependency characteristic |  | – |  | VFD | VI | VFI
24 | BB = Voltage waveform characteristic |  | –
25 | CCC= Voltage variation |  | –
SPACE UTILIZATION
26 | Height |  | mm
27 | Width |  | mm
28 | Depth |  | mm
29 | Mass |  | kg
30 | Any particular air handling or cooling requirements |  | –
31 | Mass with batteries or other storage device (if integrated) |  | kg
ENVIRONMENTAL RATINGS
32 | Minimum allowable ambient temperature |  | °C
33 | Maximum allowable ambient temperature |  | °C
34 | Minimum allowable relative humidity |  | %
35 | Maximum allowable relative humidity |  | %
REAL-TIME EFFICIENCY REPORTING
36 | Does UPS have built-in real-time efficiency reporting capability? |  | – |  | YES | NO
37 | If so, which communication protocols are used? |  | –
38 | Accuracy of real-time efficiency measurement. |  | "+/- %"
OTHER ENVIRONMENTAL CONSIDERATIONS
39 | UPS unit expected lifetime. |  | Years
40 | Would this UPS qualify for a manufacturer take-back program in the U.S.? |  | – |  | YES | NO
41 | Has a life-cycle analysis (LCA) been performed for this UPS system? |  | – |  | YES | NO
42 | If so, please provide additional information |  | –
43 | Please provide LCA documents or information for other UPS systems. |  | –
44 | Energy storage technology used |  | – |  | Flywheel | Lead-acid | Lithium-ion | Other (Please specify)
45 | Energy storage device expected lifetime |  | years
46 | Is energy storage device removable by the user? |  | – |  | YES | NO
47 | Stored energy time (back-up time at 100% rated load) for typical storage device configuration. |  | –
48 | Mass of energy storage device for typical storage device configuration. |  | kg
49 | Can storage device be recycled in the U.S.? |  | – |  | YES | NO
50 | Can storage device be separated from UPS? |  | – |  | YES | NO
EFFICIENCY TEST RESULTS (TYPE IN DIRECTLY OR USE "MEASUREMENTS" WORKSHEET) |  |  |  |  | Quantity | Percent of Rated Load
51 | Total Real Output Power (kW) at 100% Load |  | kW |  | Total Real Output Power (kW) | 100%
52 | Efficiency at 100% Load |  | – |  | Efficiency | 100%
53 | Total Real Output Power (kW) at 75% Load |  | kW |  | Total Real Output Power (kW) | 75%
54 | Efficiency at 75% Load |  | – |  | Efficiency | 75%
55 | Total Real Output Power (kW) at 50% Load |  | kW |  | Total Real Output Power (kW) | 50%
56 | Efficiency at 50% Load |  | – |  | Efficiency | 50%
57 | Total Real Output Power (kW) at 40% Load |  | kW |  | Total Real Output Power (kW) | 40%
58 | Efficiency at 40% Load |  | – |  | Efficiency | 40%
59 | Total Real Output Power (kW) at 30% Load |  | kW |  | Total Real Output Power (kW) | 30%
60 | Efficiency at 30% Load |  | – |  | Efficiency | 30%
61 | Total Real Output Power (kW) at 25% Load |  | kW |  | Total Real Output Power (kW) | 25%
62 | Efficiency at 25% Load |  | – |  | Efficiency | 25%
63 | Total Real Output Power (kW) at 20% Load |  | kW |  | Total Real Output Power (kW) | 20%
64 | Efficiency at 20% Load |  | – |  | Efficiency | 20%
65 | Total Real Output Power (kW) at 10% Load |  | kW |  | Total Real Output Power (kW) | 10%
66 | Efficiency at 10% Load |  | – |  | Efficiency | 10%
67 | Total Real Input Power (kW) at 0% Load |  | kW |  | Total Real Input Power (kW) | 0%
POWER FACTOR TEST RESULT (TYPE IN DIRECTLY OR USE "MEASUREMENTS" WORKSHEET) |  |  |  |  | Quantity | Percent of Rated Load
68 | Input Power Factor at 100% Load |  | – |  | Input Power Factor | 100%
Note on B6: Passive-standby, Line-interactive, Double-conversion, or Other (please specify)
Note on B13: Product of the r.m.s. values of voltage and current at a port.
Note on B14: Under periodic conditions, mean value, taken over one period, of the instantaneous power.
Note on B16: Input or output voltage assigned by the manufacturer for a specified operating condition.
Note on B17: Input or output frequency of the equipment assigned by the manufacturer for a specified operating condition.
Note on B23: The input or output voltage assigned by the manufacturer for a specified operating condition.
Note on B24: Input or output frequency of the equipment assigned by the manufacturer for a specified operating condition.
Note on B30: Voltage and frequency dependent (VFD) Voltage independent (VI) Voltage and frequency independent (VFI)
Note on B31: The steady-state waveform of the voltage when operating in: - normal or bypass mode (first character) and - stored energy mode (2nd character) Where each character takes form of either S, X or Y with the following meaning: “S”: voltage waveform is sinusoidal – presenting total harmonic distortion ≤ 8 % and individual harmonic distortion within limits of Table 2 (IEC standard 62040-3/FDIS) under all linear and reference non-linear load conditions. “X”: voltage waveform is sinusoidal/non-sinusoidal – meeting “S” specification under all linear load condition; – not meeting “S” specification under rated non-linear load condition. “Y”: voltage waveform is non-sinusoidal – not meeting “S” specification under reference linear load condition.
Note on B32: Describes the voltage variation caused by: - change of mode of operation (1st character) - linear load step application (2nd character) - non-linear load step application (3rd character) Where each character takes form of either 1, 2 or 3 with the following meaning: “1”: performance is required for sensitive critical loads “2”: performance is accepted by most types of critical load “3”: performance is accepted by general purpose IT loads e.g. switched-mode power supplies. (See IEC standard 62040-3/FDIS for detailed performance curves).
Note on B59: Impacts the amount of material that must be recycled.

## UPS PPDS
| IEC 62040-3 Subclause | Declared Characteristics | Manufacturer’s Declared Values
| (Where applicable) | Model (manufacturer’s reference)
General Characteristics |  | Manufacturer
Model Number
|  | Power, rated - Apparent |  | VA
|  | Active |  | W
| 5.1.1 | UPS Configuration
Topology - Passive-standby, Line-interactive, Double-conversion, or Other (please specify)
Description of normal mode under test
|  | Maximum time for UPS to switch to highest-protection mode |  | ms
Redundancy
Modularity (Minimum or Maximum configuration)
| 5.3.4 | Performance Classification
AAA = Input dependency characteristic (Voltage and frequency dependent (VFD), Voltage independent (VI) or Voltage and frequency independent (VFI))
BB = Voltage waveform characteristic
CCC= Voltage variation
Other (e.g. DC Output UPSs/Rectifier
Mechanical
|  | Dimensions (height*width*depth) |  | mm
|  | Mass |  | kg
|  | Mass with batteries (if integrated) |  | kg
Any particular air handling or cooling requirements
Environmental Conditions for Operation
| 4.2.1.1 | Ambient temperature range |  | deg C
|  | Relative humidity range |  | %
Other Environmental Considerations
Unit qualifies for a manufacturer take-back program in the U.S (Yes/No)
Link to Life-cycle analysis (LCA) and information
Communication and Measurement
| 5.6 | Communication Circuits
(List communication /signalling circuits)
Available power reporting and accuracy?
Other Data Measurements Available & Accuracy?
Available communication capabilities for efficiency reporting
Compatible protocols for data collection
Averaging method and time period
| 4.3 | Additional or unusual conditions
Output Electrical Characteristics |  | Voltage (steady state, r.m.s)
|  | -rated |  | V
|  | Nominal output voltage used for test |  | V
|  | Frequency (steady-state) - rated |  | Hz
| 5.3.2 | AC power distribution system
-compatibility (TN,TT,IT)
-phases available (1,2 or 3)
-neutral available (yes/no)
| 5.3.3 | Additional or unusual conditions
Input Electrical Characteristics | 5.2.1.a | Voltage (steady-state, r.m.s) - rated |  | V
| 5.2.1.c | Frequency (steady-state) - rated |  | Hz
|  | Nominal input voltage used for test |  | V
| 5.2.2.d | power factor
| 5.2.2.k | AC power distribution systems - (TN, TT, IT) compatibility
| 5.2.2.i | - short-circuit power required |  | Ssc
| 5.2.2.a | -phases required (1,2 or 3)
| 5.2.2.b | neutral required (yes/no)
| 5.2.3 | Additional or unusual conditions
Battery/Stored Energy Device | 5.4.2.2d | Technology
| 5.4.2.2a | Design life or float service life |  | years
| 5.4.2.2b | Quantity of cells and strings
| 5.4.2.2c | Nominal voltage (total)
| 5.4.2.2f | Stored energy time (back-up time at 100 % rated load)
| 5.4.2.2g | Restored energy time (recharge time to 90 % capacity)
Is energy storage device removable by the user?
Can storage device be recycled in the U.S.?
Can storage device be separated from UPS?
| 5.4.2..3 | Additional or unusual conditions
Power Profile* |  | Total Real Output Power (kW) at 100% Load |  | kW
|  | Efficiency at 100% Load |  | %
|  | Total Real Output Power (kW) at 75% Load |  | kW
|  | Efficiency at 80% Load |  | %
|  | Total Real Output Power (kW) at 50% Load |  | kW
|  | Efficiency at 75% Load |  | %
|  | Total Real Output Power (kW) at 50% Load |  | kW
|  | Efficiency at 70% Load |  | %
|  | Total Real Output Power (kW) at 50% Load |  | kW
|  | Efficiency at 60% Load |  | %
|  | Total Real Output Power (kW) at 50% Load |  | kW
|  | Efficiency at 50% Load |  | %
|  | Total Real Output Power (kW) at 50% Load |  | kW
|  | Efficiency at 40% Load |  | %
|  | Total Real Output Power (kW) at 30% Load |  | kW
|  | Efficiency at 30% Load |  | %
|  | Total Real Output Power (kW) at 25% Load |  | kW
|  | Efficiency at 25% Load |  | %
|  | Total Real Output Power (kW) at 20% Load |  | kW
|  | Efficiency at 20% Load |  | %
|  | Total Real Output Power (kW) at 10% Load |  | kW
|  | Efficiency at 10% Load |  | %
|  | Total Real Input Power (kW) at 0% Load |  | kW
Rectifier TEER for DC output UPSs (Maximum 1000)
* Per the ENERGY STAR Test Method for Uninterruptible Power Supplies, efficiencies at 100%,75%,50% and 25% apply to AC-output UPSs, while efficiencies at 80%, 70%, 60%, 50%, 40%, 30% and 0% apply to DC-output UPSs/Rectifiers. However, if desired, stakeholder may submit test data at additional loading points.
s
s
Note on C15: The steady-state waveform of the voltage when operating in: - normal or bypass mode (first character) and - stored energy mode (2nd character) Where each character takes form of either S, X or Y with the following meaning: “S”: voltage waveform is sinusoidal – presenting total harmonic distortion ≤ 8 % and individual harmonic distortion within limits of Table 2 (IEC standard 62040-3/FDIS) under all linear and reference non-linear load conditions. “X”: voltage waveform is sinusoidal/non-sinusoidal – meeting “S” specification under all linear load condition; – not meeting “S” specification under rated non-linear load condition. “Y”: voltage waveform is non-sinusoidal – not meeting “S” specification under reference linear load condition.
Note on C17: Describes the voltage variation caused by: - change of mode of operation (1st character) - linear load step application (2nd character) - non-linear load step application (3rd character) Where each character takes form of either 1, 2 or 3 with the following meaning: “1”: performance is required for sensitive critical loads “2”: performance is accepted by most types of critical load “3”: performance is accepted by general purpose IT loads e.g. switched-mode power supplies. (See IEC standard 62040-3/FDIS for detailed performance curves).
Note on C16: Describes the voltage variation caused by: - change of mode of operation (1st character) - linear load step application (2nd character) - non-linear load step application (3rd character) Where each character takes form of either 1, 2 or 3 with the following meaning: “1”: performance is required for sensitive critical loads “2”: performance is accepted by most types of critical load “3”: performance is accepted by general purpose IT loads e.g. switched-mode power supplies. (See IEC standard 62040-3/FDIS for detailed performance curves).